## Disclaimer
Programme Area: |  |  | Carbon Capture and Storage
Project: |  | Next Gen Capture Tech Benchmarking and Performance Analysis
Title: | Benchmarking and Performance Analysis of Future CO2 Capture Technologies – Economic Model
Abstract:
This spreadsheet model was produced as part of the CCS Capture Benchmarking Study, and provides a techno-economic analysis of the performance of four state-of-the art power generation/CO2 capture designs (coal with post-combustion capture, coal with gasification/pre-combustion capture, coal with oxy-firing and combined cycle gas turbine with post-combustion capture). The spreadsheet enables ‘what if’ calculations of costs for designs with 85%, 90% and 95% capture rates. Outputs include capital costs, operating costs, cost of capture and levelised cost of electricity (LCOE). The spreadsheet concentrates on power generation, capture and compression, but allows manual input of transport and storage costs to provide overall figures. The model is partly superseded by work undertaken and reported in the Benchmark Refresh project.
Context:
This project provided ETI with an objective view of the techno-economic performance of a range of current and next generation CO2 capture technologies including pre and post combustion and oxyfuel CCS plant. The analysis that underpins these benchmarking studies was based on coal and gas fired power station designs typical of those found in the UK and considered parameters such as power station capital cost, efficiency and levelised cost of electricity (with and without CCS).
Disclaimer:
The Energy Technologies Institute is making this document available to use under the Energy Technologies Institute Open Licence for Materials. Please refer to the Energy Technologies Institute website for the terms and conditions of this licence. The Information is licensed ‘as is’ and the Energy Technologies Institute excludes all representations, warranties, obligations and liabilities in relation to the Information to the maximum extent permitted by law. The Energy Technologies Institute is not liable for any errors or omissions in the Information and shall not be liable for any loss, injury or damage of any kind caused by its use. This exclusion of liability includes, but is not limited to, any direct, indirect, special, incidental, consequential, punitive, or exemplary damages in each case such as loss of revenue, data, anticipated profits, and lost business. The Energy Technologies Institute does not guarantee the continued supply of the Information. Notwithstanding any statement to the contrary contained on the face of this document, the Energy Technologies Institute confirms that the authors of the document have consented to its publication by the Energy Technologies Institute.

## Title Page
THE ENERGY TECHNOLOGIES INSTITUTE
Benchmarking and Performance Analysis of Next Generation Carbon Capture Technologies
Economic Model

## Contents
Benchmarking and Performance Analysis of Next Generation Carbon Capture Technologies
General Information |  | Model Contents
|  | Title Page | Introduction page
Author | Tim Bullen, Foster Wheeler | Contents | This page, tracks version control and changes
Purpose |  | Input Data | General input values for all calculations & scenario selection.
Scope |  | IGCC with CC | Cash flow analysis for the IGCC case with carbon capture
Basis |  | IGCC without CC | Cash flow analysis for the IGCC case without carbon capture
|  | CCGT with 90% CC | Cash flow analysis for the CCGT case with 90% carbon capture
Version Control |  | CCGT with 75% CC | Cash flow analysis for the CCGT case with 75% carbon capture
|  | CCGT without CC | Cash flow analysis for the CCGT case without carbon capture
Status | Final | USCPC with CC | Cash flow analysis for the USCPC case with carbon capture
Release Date | 3rd November 2009 | USCPC without CC | Cash flow analysis for the USCPC case without carbon capture
Version Number | 1 | Oxyfuel with CC | Cash flow analysis for the oxyfuel case with carbon capture
Version History | 1.0 - Amendment to CAPEX estimate for WP1 report | Summary Results | Summary of key results
Running Procedures
Comments |  | Save the file under a new filename
Enter a unique identifier for the dataset
Enter any required adjustments on the "Input Data" dataset only. Update the individual economic
model sheets by pressing the "Update Economic Model" button.
Check data and verify reports. Print out required reports

## Input Data
Benchmarking and Performance Analysis of Next Generation Carbon Capture Technologies
Input Data
[5 empty] | IGCC with CC | [5 empty] | IGCC without CC | [5 empty] | CCGT with 90% CC |  |  |  |  | CCGT without CC |  |  |  |  | USCPC with CC |  |  |  |  | USCPC without CC |  |  |  |  | OxyFuel |  |  |  |  | CCGT with 75% CC
|  |  |  | Raw Value | Adj. Factor | Adjusted Value |  |  |  | Raw Value | Adj. Factor | Adjusted Value |  |  |  | Raw Value | Adj. Factor | Adjusted Value |  |  | Raw Value | Adj. Factor | Adjusted Value |  |  | Raw Value | Adj. Factor | Adjusted Value |  |  | Raw Value | Adj. Factor | Adjusted Value |  |  | Raw Value | Adj. Factor | Adjusted Value |  |  | Raw Value | Adj. Factor | Adjusted Value
Data From Process Simulations
Power / Performance Data | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
Installed Gross Capacity |  |  | MWe | 923.8 | n/a | 923.8 |  |  |  | 878.1 | n/a | 878.1 |  |  |  | 955.3 | n/a | 955.3 |  |  | 1037.6 | n/a | 1037.6 |  |  | 745.7 | n/a | 745.7 |  |  | 836.2 | n/a | 836.2 |  |  | 855.4 | n/a | 855.4 |  |  | 970.7 | n/a | 970.7
| Gas Turbines |  | MWe | 544.4 | n/a | 544.4 |  |  |  | 514.5 | n/a | 514.5 |  |  |  | 729.1 | n/a | 729.1 |  |  | 729.1 | n/a | 729.1 |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | 729.1 | n/a | 729.1
| Steam Turbine |  | MWe | 379.4 | n/a | 379.4 |  |  |  | 363.6 | n/a | 363.6 |  |  |  | 226.2 | n/a | 226.2 |  |  | 308.5 | n/a | 308.5 |  |  | 745.7 | n/a | 745.7 |  |  | 836.2 | n/a | 836.2 |  |  | 855.4 | n/a | 855.4 |  |  | 241.6 | n/a | 241.6
| Expansion Turbine |  | MWe | 0 | n/a | 0 |  |  |  | 0 | n/a | 0 |  |  |  | 0 | n/a | 0 |  |  | 0 | n/a | #VALUE! |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | n/a | 0
Total Auxiliary Load |  |  | MWe | 223.7 | n/a | 223.7 |  |  |  | 132 | n/a | 132 |  |  |  | 113 | n/a | 113 |  |  | 46.8 | n/a | 46.8 |  |  | 119 | n/a | 119 |  |  | 57 | n/a | 57 |  |  | 249.8 | n/a | 249.8 |  |  | 98.4 | n/a | 98.4
| Air Separation Unit |  | MWe | 101.6 | 1 | 101.6 |  |  |  | 95.7 | 1 | 95.7 |  |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | 91.5 | 1 | 91.5 |  |  | n/a | n/a | n/a
| Gasification island / Boiler |  | MWe | 13 | 1 | 13 |  |  |  | 11.6 | 1 | 11.6 |  |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a
| Power Island |  | MWe | 7.6 | 1 | 7.6 |  |  |  | 10.5 | 1 | 10.5 |  |  |  | 39.3 | 1 | 39.3 |  |  | 40.1 | 1 | 40.1 |  |  | 29 | 1 | 29 |  |  | 29.1 | 1 | 29.1 |  |  | 28.2 | 1 | 28.2 |  |  | 39.4 | 1 | 39.4
| Acid Gas Removal Unit |  | MWe | 30.8 | 1 | 30.8 |  |  |  | 0.3 | 1 | 0.3 |  |  |  | 32.8 | 1 | 32.8 |  |  | n/a | n/a | n/a |  |  | 7.4 | 1 | 7.4 |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | 27.4 | 1 | 27.4
| CO2 Compression |  | MWe | 47.9 | 1 | 47.9 |  |  |  | n/a | n/a | n/a |  |  |  | 27.7 | 1 | 27.7 |  |  | 0 | 1 | 0 |  |  | 48.6 | 1 | 48.6 |  |  | n/a | n/a | n/a |  |  | 91.4 | 1 | 91.4 |  |  | 23.2 | 1 | 23.2
| Other Units (offsites & Utilities) |  | MWe | 22.8 | 1 | 22.8 |  |  |  | 13.9 | 1 | 13.9 |  |  |  | 13.2 | 1 | 13.2 |  |  | 6.7 | 1 | 6.7 |  |  | 34 | 1 | 34 |  |  | 27.9 | 1 | 27.9 |  |  | 38.7 | 1 | 38.7 |  |  | 8.4 | 1 | 8.4
Gross Power Output |  |  | MWe | 923.8 | n/a | 923.8 |  |  |  | 878.1 | n/a | 878.1 |  |  |  | 955.3 | n/a | 955.3 |  |  | 1037.6 | n/a | 1037.6 |  |  | 745.7 | n/a | 745.7 |  |  | 836.2 | n/a | 836.2 |  |  | 855.4 | n/a | 855.4 |  |  | 970.7 | n/a | 970.7
Net Power Export (New & Clean) |  |  | MWe | 700.1 | n/a | 700.1 |  |  |  | 746.1 | n/a | 746.1 |  |  |  | 842.3 | n/a | 842.3 |  |  | 990.8 | n/a | 990.8 |  |  | 626.7 | n/a | 626.7 |  |  | 779.2 | n/a | 779.2 |  |  | 605.6 | n/a | 605.6 |  |  | 872.3 | n/a | 872.3
Feedstocks
| Feedstock rate | Coal | te/hr | 273.2917 | n/a | 273.2917 |  |  |  | 230.7917 | n/a | 230.7917 |  |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | 256.7917 | n/a | 256.7917 |  |  | 256.7917 | n/a | 256.7917 |  |  | 257 | n/a | 257 |  |  | n/a | n/a | n/a
|  | Natural Gas | te/hr | n/a | n/a | n/a |  |  |  | n/a | n/a | n/a |  |  |  | 127.9167 | n/a | 127.9167 |  |  | 127.9167 | n/a | 127.9167 |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | 127.9167 | n/a | 127.9167
| Oxygen Consumption |  | te/hr | 196.2083 | n/a | 196.2083 |  |  |  | 176.7917 | n/a | 176.7917 |  |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | 569 | n/a | 569 |  |  | n/a | n/a | n/a
Carbon Dioxide
| CO2 Produced |  | te/hr | 647.2083 | n/a | 647.2083 |  |  |  | 548 | n/a | 548 |  |  |  | 346.8333 | n/a | 346.8333 |  |  | 347 | n/a | 347 |  |  | 608.1667 | n/a | 608.1667 |  |  | 608 | n/a | 608 |  |  | 607.9 | n/a | 607.9 |  |  | 347.1 | n/a | 347.1
| CO2 Captured |  | te/hr | 582.3333 | n/a | 582.3333 |  |  |  | 0 | n/a | 0 |  |  |  | 312.8333 | n/a | 312.8333 |  |  | 0 | n/a | 0 |  |  | 547.1667 | n/a | 547.1667 |  |  | 0 | n/a | 0 |  |  | 549.3167 | n/a | 549.3167 |  |  | 261.1 | n/a | 261.1
| CO2 Emissions |  | te/hr | 64.875 | n/a | 64.875 |  |  |  | 548 | n/a | 548 |  |  |  | 34 | n/a | 34 |  |  | 347 | n/a | 347 |  |  | 61 | n/a | 61 |  |  | 608 | n/a | 608 |  |  | 58.5833 | n/a | 58.5833 |  |  | 86 | n/a | 86
| Specific CO2 Emissions |  | g / kWhr (Net) | 92.7 | n/a | 92.7 |  |  |  | 735 | n/a | 735 |  |  |  | 41 | n/a | 41 |  |  | 350 | n/a | 350 |  |  | 97 | n/a | 97 |  |  | 781 | n/a | 781 |  |  | 96.7 | n/a | 96.7 |  |  | 98.5 | n/a | 98.5
Other Products
| Sulphur Produced |  | te/hr | 2.3 | n/a | 2.3 |  |  |  | 1.95 | n/a | 1.95 |  |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a
| Hydrogen Produced (ex syngas production unit) |  | te/hr | 133.8 | n/a | 133.8 |  |  |  | 398.3 | n/a | 398.3 |  |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a
Waste |  |  | te/hr | 42 | n/a | 42 |  |  |  | 35.6 | n/a | 35.6 |  |  |  | 0 | n/a | 0 |  |  | 0 | n/a | 0 |  |  | 33 | n/a | 33 |  |  | 33 | n/a | 33 |  |  | 33 | n/a | 33 |  |  | 0 | n/a | 0
User Input Variables
Data From CAPEX and OPEX Estimates
Capital Cost Data | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
| Coal Drying | Installed Cost | UK£(million) | 0 | 1 | 0 |  |  |  | 0 | 1 | 0 |  |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0
| Gasification | Installed Cost | UK£(million) | 238.9 | 1 | 238.9 |  |  |  | 214.5 | 1 | 214.5 |  |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 556.7 | 1 | 556.7 |  |  | 550.5 | 1 | 550.5 |  |  | 556.7 | 1 | 556.7 |  |  | 0 | 1 | 0
| Air Separation | Installed Cost | UK£(million) | 104.1 | 1 | 104.1 |  |  |  | 92.8 | 1 | 92.8 |  |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 241.7 | 1 | 241.7 |  |  | 0 | 1 | 0
| Acid Gas Removal | Installed Cost | UK£(million) | 121 | 1 | 121 |  |  |  | 62.5 | 1 | 62.5 |  |  |  | 240.9 | 1 | 240.9 |  |  | 0 | 1 | 0 |  |  | 262.1 | 1 | 262.1 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 214 | 1 | 214
| CO2 Compression Unit | Installed Cost | UK£(million) | 61.7 | 1 | 61.7 |  |  |  | 0 | 1 | 0 |  |  |  | 69.5 | 1 | 69.5 |  |  | 0 | 1 | 0 |  |  | 90.6 | 1 | 90.6 |  |  | 0 | 1 | 0 |  |  | 155.6 | 1 | 155.6 |  |  | 61.9 | 1 | 61.9
| CO2 Drying Unit | Installed Cost | UK£(million) | 0 | 1 | 0 |  |  |  | 0 | 1 | 0 |  |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0
| Sulphur Plant | Installed Cost | UK£(million) | 33.1 | 1 | 33.1 |  |  |  | 29.6 | 1 | 29.6 |  |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0
| Power Island | Installed Cost | UK£(million) | 341.1 | 1 | 341.1 |  |  |  | 341.8 | 1 | 341.8 |  |  |  | 319.7 | 1 | 319.7 |  |  | 302.5 | 1 | 302.5 |  |  | 150.9 | 1 | 150.9 |  |  | 185.3 | 1 | 185.3 |  |  | 167.5 | 1 | 167.5 |  |  | 319.7 | 1 | 319.7
| Syngas Treatment Plant | Installed Cost | UK£(million) | 66 | 1 | 66 |  |  |  | 46.2 | 1 | 46.2 |  |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0 |  |  | 0 | 1 | 0
| Offsite & Utilities | Installed Cost | UK£(million) | 145.6 | 1 | 145.6 |  |  |  | 122.6 | 1 | 122.6 |  |  |  | 101.3 | 1 | 101.3 |  |  | 86.4 | 1 | 86.4 |  |  | 87.9 | 1 | 87.9 |  |  | 78.3 | 1 | 78.3 |  |  | 233.2 | 1 | 233.2 |  |  | 101.3 | 1 | 101.3
| TOTAL | Installed Cost | UK£(million) | 1111.5 | n/a | 1111.5 |  |  |  | 910 | n/a | 910 |  |  |  | 731.4 | n/a | 731.4 |  |  | 388.9 | n/a | 388.9 |  |  | 1148.2 | n/a | 1148.2 |  |  | 814.1 | n/a | 814.1 |  |  | 1354.7 | n/a | 1354.7 |  |  | 696.9 | n/a | 696.9
[6 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
| Contingency |  |  | 25% | 1 | 25% |  |  |  | 25% | 1 | 25% |  |  |  | 25% | 1 | 25% |  |  | 25% | 1 | 25% |  |  | 25% | 1 | 25% |  |  | 25% | 1 | 25% |  |  | 25% | 1 | 25% |  |  | 25% | 1 | 25%
| Land purchase, surveys |  |  | 5% | 1 | 5% |  |  |  | 5% | 1 | 5% |  |  |  | 5% | 1 | 5% |  |  | 5% | 1 | 5% |  |  | 5% | 1 | 5% |  |  | 5% | 1 | 5% |  |  | 5% | 1 | 5% |  |  | 5% | 1 | 5%
| Fees |  |  | 10% | 1 | 10% |  |  |  | 10% | 1 | 10% |  |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10%
| Discounted Rate |  |  | 10% | 1 | 10% |  |  |  | 10% | 1 | 10% |  |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10%
Operating Cost Data
[6 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
| Coal Price |  | UK£/te | 65 | 1 | 65 |  |  |  | 65 | 1 | 65 |  |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | 65 | 1 | 65 |  |  | 65 | 1 | 65 |  |  | 65 | 1 | 65 |  |  | n/a | n/a | n/a
| Maintenance |  | UK£(million)/year | 39.72 | 1 | 39.72 |  |  |  | 34.22 | 1 | 34.22 |  |  |  | 25.5 | 1 | 25.5 |  |  | 16.6 | 1 | 16.6 |  |  | 40.1 | 1 | 40.1 |  |  | 32.6 | 1 | 32.6 |  |  | 44.5 | 1 | 44.5 |  |  | 24.6 | 1 | 24.6
| Waste Disposal |  | UK£/te | 6 | 1 | 6 |  |  |  | 6 | 1 | 6 |  |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | 6 | 1 | 6 |  |  | 6 | 1 | 6 |  |  | 6 | 1 | 6 |  |  | n/a | n/a | n/a
| Chemicals & Consumables |  | UK£(million)/year | 3.79 | 1 | 3.79 |  |  |  | 2.48 | 1 | 2.48 |  |  |  | 1.2 | 1 | 1.2 |  |  | 0.001 | 1 | 0.001 |  |  | 15.2 | 1 | 15.2 |  |  | 5.7 | 1 | 5.7 |  |  | 0.1 | 1 | 0.1 |  |  | 0.98 | 1 | 0.98
| Natural Gas Price |  | UK£/te | n/a | 1 | n/a |  |  |  | n/a | n/a | n/a |  |  |  | 265 | 1 | 265 |  |  | 265 | 1 | 265 |  |  | n/a | 1 | n/a |  |  | n/a | 1 | n/a |  |  | n/a | 1 | n/a |  |  | 265 | 1 | 265
| CO2 Emissions |  | UK£/te | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
| Number of operations personnel |  |  | 128 | 1 | 128 |  |  |  | 115 | 1 | 115 |  |  |  | 60 | 1 | 60 |  |  | 40 | 1 | 40 |  |  | 115 | 1 | 115 |  |  | 105 | 1 | 105 |  |  | 128 | 1 | 128 |  |  | 60 | 1 | 60
| Average salary options personnel |  |  | 0.05 | 1 | 0.05 |  |  |  | 0.05 | 1 | 0.05 |  |  |  | 0.05 | 1 | 0.05 |  |  | 0.05 | 1 | 0.05 |  |  | 0.05 | 1 | 0.05 |  |  | 0.05 | 1 | 0.05 |  |  | 0.05 | 1 | 0.05 |  |  | 0.05 | 1 | 0.05
| Admin allowance (% of operation personnel cost) |  |  | 30% | 1 | 30% |  |  |  | 30% | 1 | 30% |  |  |  | 30% | 1 | 30% |  |  | 30% | 1 | 30% |  |  | 30% | 1 | 30% |  |  | 30% | 1 | 30% |  |  | 30% | 1 | 30% |  |  | 30% | 1 | 30%
| Insurance |  |  | 2% | 1 | 2% |  |  |  | 2% | 1 | 2% |  |  |  | 2% | 1 | 2% |  |  | 2% | 1 | 2% |  |  | 2% | 1 | 2% |  |  | 2% | 1 | 2% |  |  | 2% | 1 | 2% |  |  | 2% | 1 | 2%
Revenue Variables | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
| Sulphur Price |  | UK£/te | 40 | 1 | 40 |  |  |  | 40 | 1 | 40 |  |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a
| Hydrogen Price |  | UK£/te | 1307.1895 | 1 | 1307.1895 |  |  |  | 1307.1895 | 1 | 1307.1895 |  |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a |  |  | n/a | n/a | n/a
| Discount Rate |  | % | 10% | 1 | 10% |  |  |  | 10% | 1 | 10% |  |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10% |  |  | 10% | 1 | 10%
[5 empty] | 30 | [5 empty] | 30 | [5 empty] | 20 |  |  |  |  | 20 |  |  |  |  | 30 |  |  |  |  | 30 |  |  |  |  | 30 |  |  |  |  | 20
Project Life (can be 20, 25 or 30 years) |  |  | years | 30 | 0 | 30 |  |  |  | 30 | 0 | 30 |  |  |  | 20 | 0 | 20 |  |  | 20 | 0 | 20 |  |  | 30 | 0 | 30 |  |  | 30 | 0 | 30 |  |  | 30 | 0 | 30 |  |  | 20 | 0 | 20
Project Internal Rate of Return
Year 1 of Plant | [5 empty] | 2012 | [5 empty] | 2012 | [5 empty] | 2012 |  |  |  |  | 2012 |  |  |  |  | 2012 |  |  |  |  | 2012 |  |  |  |  | 2012 |  |  |  |  | 2012
Expenditure factor
| Start Project year 1 |  |  |  |  | 25% | [5 empty] | 25% | [5 empty] | 25% |  |  |  |  | 25% |  |  |  |  | 25% |  |  |  |  | 25% |  |  |  |  | 25% |  |  |  |  | 25%
| Start Project year 2 |  |  |  |  | 45% | [5 empty] | 45% | [5 empty] | 45% |  |  |  |  | 45% |  |  |  |  | 45% |  |  |  |  | 45% |  |  |  |  | 45% |  |  |  |  | 45%
| Start Project year 3 |  |  |  |  | 30% | [5 empty] | 30% | [5 empty] | 30% |  |  |  |  | 30% |  |  |  |  | 30% |  |  |  |  | 30% |  |  |  |  | 30% |  |  |  |  | 30%
Factors |  |  |  | Load |  | Availability |  |  |  | Load |  | Availability |  |  |  | Load | Availability |  |  |  | Load | Availability |  |  |  | Load | Availability |  |  |  | Load | Availability |  |  |  | Load | Availability |  |  |  | Load | Availability
|  |  |  | H2 Prod'n | Power Island | H2 Prod'n | Power Island |  |  | H2 Prod'n | Power Island | H2 Prod'n | Power Island
|  | Year 1 | 2012 | 1 | 1 | 0.65 | 0.65 | Year 1 | 2012 | 1 | 1 | 0.65 | 0.65 | Year 1 | 2012 | 1 | 0.65 |  | Year 1 | 2012 | 1 | 0.65 |  | Year 1 | 2012 | 1 | 0.65 |  | Year 1 | 2012 | 1 | 0.65 |  | Year 1 | 2012 | 1 | 0.65 |  | Year 1 | 2012 | 1 | 0.65
|  | Year 2 | 2013 | 1 | 1 | 0.75 | 0.75 | Year 2 | 2013 | 1 | 1 | 0.75 | 0.75 | Year 2 | 2013 | 1 | 0.75 |  | Year 2 | 2013 | 1 | 0.75 |  | Year 2 | 2013 | 1 | 0.75 |  | Year 2 | 2013 | 1 | 0.75 |  | Year 2 | 2013 | 1 | 0.75 |  | Year 2 | 2013 | 1 | 0.75
|  | Year 3 | 2014 | 1 | 1 | 0.85 | 0.85 | Year 3 | 2014 | 1 | 1 | 0.85 | 0.85 | Year 3 | 2014 | 1 | 0.85 |  | Year 3 | 2014 | 1 | 0.85 |  | Year 3 | 2014 | 1 | 0.85 |  | Year 3 | 2014 | 1 | 0.85 |  | Year 3 | 2014 | 1 | 0.85 |  | Year 3 | 2014 | 1 | 0.85
|  | Year 4 | 2015 | 1 | 1 | 0.85 | 0.85 | Year 4 | 2015 | 1 | 1 | 0.85 | 0.85 | Year 4 | 2015 | 1 | 0.85 |  | Year 4 | 2015 | 1 | 0.85 |  | Year 4 | 2015 | 1 | 0.85 |  | Year 4 | 2015 | 1 | 0.85 |  | Year 4 | 2015 | 1 | 0.85 |  | Year 4 | 2015 | 1 | 0.85
|  | Year 5 | 2016 | 1 | 1 | 0.85 | 0.85 | Year 5 | 2016 | 1 | 1 | 0.85 | 0.85 | Year 5 | 2016 | 1 | 0.85 |  | Year 5 | 2016 | 1 | 0.85 |  | Year 5 | 2016 | 1 | 0.85 |  | Year 5 | 2016 | 1 | 0.85 |  | Year 5 | 2016 | 1 | 0.85 |  | Year 5 | 2016 | 1 | 0.85
|  | Year 6 | 2017 | 1 | 1 | 0.85 | 0.85 | Year 6 | 2017 | 1 | 1 | 0.85 | 0.85 | Year 6 | 2017 | 1 | 0.85 |  | Year 6 | 2017 | 1 | 0.85 |  | Year 6 | 2017 | 1 | 0.85 |  | Year 6 | 2017 | 1 | 0.85 |  | Year 6 | 2017 | 1 | 0.85 |  | Year 6 | 2017 | 1 | 0.85
|  | Year 7 | 2018 | 1 | 1 | 0.85 | 0.85 | Year 7 | 2018 | 1 | 1 | 0.85 | 0.85 | Year 7 | 2018 | 1 | 0.85 |  | Year 7 | 2018 | 1 | 0.85 |  | Year 7 | 2018 | 1 | 0.85 |  | Year 7 | 2018 | 1 | 0.85 |  | Year 7 | 2018 | 1 | 0.85 |  | Year 7 | 2018 | 1 | 0.85
|  | Year 8 | 2019 | 1 | 1 | 0.85 | 0.85 | Year 8 | 2019 | 1 | 1 | 0.85 | 0.85 | Year 8 | 2019 | 1 | 0.85 |  | Year 8 | 2019 | 1 | 0.85 |  | Year 8 | 2019 | 1 | 0.85 |  | Year 8 | 2019 | 1 | 0.85 |  | Year 8 | 2019 | 1 | 0.85 |  | Year 8 | 2019 | 1 | 0.85
|  | Year 9 | 2020 | 1 | 1 | 0.85 | 0.85 | Year 9 | 2020 | 1 | 1 | 0.85 | 0.85 | Year 9 | 2020 | 1 | 0.85 |  | Year 9 | 2020 | 1 | 0.85 |  | Year 9 | 2020 | 1 | 0.85 |  | Year 9 | 2020 | 1 | 0.85 |  | Year 9 | 2020 | 1 | 0.85 |  | Year 9 | 2020 | 1 | 0.85
|  | Year 10 | 2021 | 1 | 1 | 0.85 | 0.85 | Year 10 | 2021 | 1 | 1 | 0.85 | 0.85 | Year 10 | 2021 | 1 | 0.85 |  | Year 10 | 2021 | 1 | 0.85 |  | Year 10 | 2021 | 1 | 0.85 |  | Year 10 | 2021 | 1 | 0.85 |  | Year 10 | 2021 | 1 | 0.85 |  | Year 10 | 2021 | 1 | 0.85
|  | Year 11 | 2022 | 1 | 1 | 0.85 | 0.85 | Year 11 | 2022 | 1 | 1 | 0.85 | 0.85 | Year 11 | 2022 | 1 | 0.85 |  | Year 11 | 2022 | 1 | 0.85 |  | Year 11 | 2022 | 1 | 0.85 |  | Year 11 | 2022 | 1 | 0.85 |  | Year 11 | 2022 | 1 | 0.85 |  | Year 11 | 2022 | 1 | 0.85
|  | Year 12 | 2023 | 1 | 1 | 0.85 | 0.85 | Year 12 | 2023 | 1 | 1 | 0.85 | 0.85 | Year 12 | 2023 | 1 | 0.85 |  | Year 12 | 2023 | 1 | 0.85 |  | Year 12 | 2023 | 1 | 0.85 |  | Year 12 | 2023 | 1 | 0.85 |  | Year 12 | 2023 | 1 | 0.85 |  | Year 12 | 2023 | 1 | 0.85
|  | Year 13 | 2024 | 1 | 1 | 0.85 | 0.85 | Year 13 | 2024 | 1 | 1 | 0.85 | 0.85 | Year 13 | 2024 | 1 | 0.85 |  | Year 13 | 2024 | 1 | 0.85 |  | Year 13 | 2024 | 1 | 0.85 |  | Year 13 | 2024 | 1 | 0.85 |  | Year 13 | 2024 | 1 | 0.85 |  | Year 13 | 2024 | 1 | 0.85
|  | Year 14 | 2025 | 1 | 1 | 0.85 | 0.85 | Year 14 | 2025 | 1 | 1 | 0.85 | 0.85 | Year 14 | 2025 | 1 | 0.85 |  | Year 14 | 2025 | 1 | 0.85 |  | Year 14 | 2025 | 1 | 0.85 |  | Year 14 | 2025 | 1 | 0.85 |  | Year 14 | 2025 | 1 | 0.85 |  | Year 14 | 2025 | 1 | 0.85
|  | Year 15 | 2026 | 1 | 1 | 0.85 | 0.85 | Year 15 | 2026 | 1 | 1 | 0.85 | 0.85 | Year 15 | 2026 | 1 | 0.85 |  | Year 15 | 2026 | 1 | 0.85 |  | Year 15 | 2026 | 1 | 0.85 |  | Year 15 | 2026 | 1 | 0.85 |  | Year 15 | 2026 | 1 | 0.85 |  | Year 15 | 2026 | 1 | 0.85
|  | Year 16 | 2027 | 1 | 1 | 0.85 | 0.85 | Year 16 | 2027 | 1 | 1 | 0.85 | 0.85 | Year 16 | 2027 | 1 | 0.85 |  | Year 16 | 2027 | 1 | 0.85 |  | Year 16 | 2027 | 1 | 0.85 |  | Year 16 | 2027 | 1 | 0.85 |  | Year 16 | 2027 | 1 | 0.85 |  | Year 16 | 2027 | 1 | 0.85
|  | Year 17 | 2028 | 1 | 1 | 0.85 | 0.85 | Year 17 | 2028 | 1 | 1 | 0.85 | 0.85 | Year 17 | 2028 | 1 | 0.85 |  | Year 17 | 2028 | 1 | 0.85 |  | Year 17 | 2028 | 1 | 0.85 |  | Year 17 | 2028 | 1 | 0.85 |  | Year 17 | 2028 | 1 | 0.85 |  | Year 17 | 2028 | 1 | 0.85
|  | Year 18 | 2029 | 1 | 1 | 0.85 | 0.85 | Year 18 | 2029 | 1 | 1 | 0.85 | 0.85 | Year 18 | 2029 | 1 | 0.85 |  | Year 18 | 2029 | 1 | 0.85 |  | Year 18 | 2029 | 1 | 0.85 |  | Year 18 | 2029 | 1 | 0.85 |  | Year 18 | 2029 | 1 | 0.85 |  | Year 18 | 2029 | 1 | 0.85
|  | Year 19 | 2030 | 1 | 1 | 0.85 | 0.85 | Year 19 | 2030 | 1 | 1 | 0.85 | 0.85 | Year 19 | 2030 | 1 | 0.85 |  | Year 19 | 2030 | 1 | 0.85 |  | Year 19 | 2030 | 1 | 0.85 |  | Year 19 | 2030 | 1 | 0.85 |  | Year 19 | 2030 | 1 | 0.85 |  | Year 19 | 2030 | 1 | 0.85
|  | Year 20 | 2031 | 1 | 1 | 0.85 | 0.85 | Year 20 | 2031 | 1 | 1 | 0.85 | 0.85 | Year 20 | 2031 | 1 | 0.85 |  | Year 20 | 2031 | 1 | 0.85 |  | Year 20 | 2031 | 1 | 0.85 |  | Year 20 | 2031 | 1 | 0.85 |  | Year 20 | 2031 | 1 | 0.85 |  | Year 20 | 2031 | 1 | 0.85
|  | Year 21 | 2032 | 1 | 1 | 0.85 | 0.85 | Year 21 | 2032 | 1 | 1 | 0.85 | 0.85 | Year 21 | 2032 | 1 | 0.85 |  | Year 21 | 2032 | 1 | 0.85 |  | Year 21 | 2032 | 1 | 0.85 |  | Year 21 | 2032 | 1 | 0.85 |  | Year 21 | 2032 | 1 | 0.85 |  | Year 21 | 2032 | 1 | 0.85
|  | Year 22 | 2033 | 1 | 1 | 0.85 | 0.85 | Year 22 | 2033 | 1 | 1 | 0.85 | 0.85 |  |  | 1 | 0.85 |  |  |  | 1 | 0.85 |  | Year 22 | 2033 | 1 | 0.85 |  | Year 22 | 2033 | 1 | 0.85 |  | Year 22 | 2033 | 1 | 0.85 |  |  |  | 1 | 0.85
|  | Year 23 | 2034 | 1 | 1 | 0.85 | 0.85 | Year 23 | 2034 | 1 | 1 | 0.85 | 0.85 |  |  | 1 | 0.85 |  |  |  | 1 | 0.85 |  | Year 23 | 2034 | 1 | 0.85 |  | Year 23 | 2034 | 1 | 0.85 |  | Year 23 | 2034 | 1 | 0.85 |  |  |  | 1 | 0.85
|  | Year 24 | 2035 | 1 | 1 | 0.85 | 0.85 | Year 24 | 2035 | 1 | 1 | 0.85 | 0.85 |  |  | 1 | 0.85 |  |  |  | 1 | 0.85 |  | Year 24 | 2035 | 1 | 0.85 |  | Year 24 | 2035 | 1 | 0.85 |  | Year 24 | 2035 | 1 | 0.85 |  |  |  | 1 | 0.85
|  | Year 25 | 2036 | 1 | 1 | 0.85 | 0.85 | Year 25 | 2036 | 1 | 1 | 0.85 | 0.85 |  |  | 1 | 0.85 |  |  |  | 1 | 0.85 |  | Year 25 | 2036 | 1 | 0.85 |  | Year 25 | 2036 | 1 | 0.85 |  | Year 25 | 2036 | 1 | 0.85 |  |  |  | 1 | 0.85
|  | Year 26 | 2037 | 1 | 1 | 0.85 | 0.85 | Year 26 | 2037 | 1 | 1 | 0.85 | 0.85 |  |  | 1 | 0.85 |  |  |  | 1 | 0.85 |  | Year 26 | 2037 | 1 | 0.85 |  | Year 26 | 2037 | 1 | 0.85 |  | Year 26 | 2037 | 1 | 0.85 |  |  |  | 1 | 0.85
|  | Year 27 | 2038 | 1 | 1 | 0.85 | 0.85 | Year 27 | 2038 | 1 | 1 | 0.85 | 0.85 |  |  | 1 | 0.85 |  |  |  | 1 | 0.85 |  | Year 27 | 2038 | 1 | 0.85 |  | Year 27 | 2038 | 1 | 0.85 |  | Year 27 | 2038 | 1 | 0.85 |  |  |  | 1 | 0.85
|  | Year 28 | 2039 | 1 | 1 | 0.85 | 0.85 | Year 28 | 2039 | 1 | 1 | 0.85 | 0.85 |  |  | 1 | 0.85 |  |  |  | 1 | 0.85 |  | Year 28 | 2039 | 1 | 0.85 |  | Year 28 | 2039 | 1 | 0.85 |  | Year 28 | 2039 | 1 | 0.85 |  |  |  | 1 | 0.85
|  | Year 29 | 2040 | 1 | 1 | 0.85 | 0.85 | Year 29 | 2040 | 1 | 1 | 0.85 | 0.85 |  |  | 1 | 0.85 |  |  |  | 1 | 0.85 |  | Year 29 | 2040 | 1 | 0.85 |  | Year 29 | 2040 | 1 | 0.85 |  | Year 29 | 2040 | 1 | 0.85 |  |  |  | 1 | 0.85
|  | Year 30 | 2041 | 1 | 1 | 0.85 | 0.85 | Year 30 | 2041 | 1 | 1 | 0.85 | 0.85 |  |  | 1 | 0.85 |  |  |  | 1 | 0.85 |  | Year 30 | 2041 | 1 | 0.85 |  | Year 30 | 2041 | 1 | 0.85 |  | Year 30 | 2041 | 1 | 0.85 |  |  |  | 1 | 0.85
|  | Year 31 | 2042 | 1 | 1 | 0.85 | 0.85 | Year 31 | 2042 | 1 | 1 | 0.85 | 0.85 |  |  | 1 | 0.85 |  |  |  | 1 | 0.85 |  | Year 31 | 2042 | 1 | 0.85 |  | Year 31 | 2042 | 1 | 0.85 |  | Year 31 | 2042 | 1 | 0.85 |  |  |  | 1 | 0.85
Update Economic Model

## IGCC w CC
Production |  |  |  | Capital Expenditure |  | UK£ (million) |  | Operating Costs | UK£ (million/year) |  |  |  | Revenues
Coal feedrate | te/h | 273.2917 |  | Installed cost |  | 1111.5 |  | Fuel Cost |  | 65 | UK£/te |  | Levelised Cost of Electricity | UK£/kWh | 0.076208
Net power ouput | MW | 700.1 |  | Land purchase, surveys |  | 5% |  | Maintenance |  | 39.72 | UK£/year |  | Sulphur Price | UK£/te | 40
Sulphur for export | te/h | 2.3 |  | Fees |  | 10% |  | CO2 Emissions |  | 0 | UK£/te |  | Hydrogen Price | UK£/te | 1307.1895
|  |  |  | Contingencies |  | 25% |  | Labour Cost |  |  | UK£/year (million)
[8 empty] | Number of operations personnel |  |  | 128 |  | Discounted Rate: |  | 10%
|  |  |  | Total Investment Cost |  | 1556.1 |  | Average salary options personnel |  |  | 0.05 |  | Insurance |  | 2% | Installed Cost
[8 empty] | Admin |  |  | 30%
[8 empty] | Total Labour Cost |  |  | 8.32
YEAR
CASH FLOW ANALYSIS |  |  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
UK£ (million) |  |  | Year -3 | Year -2 | Year -1 | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31
Load factor - Hydrogen Production | [5 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Load factor - Power Island | [5 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Availability - Hydrogen Production | [5 empty] | 65% | 75% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
Availability - Power Island | [5 empty] | 65% | 75% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
Equivalent yearly hours - Hydrogen Production | [5 empty] | 5694 | 6570 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446
Equivalent yearly hours - Power Island | [5 empty] | 5694 | 6570 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446
Hydrogen Exported |  | tpa |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Expenditure factor |  |  | YEAR 2009 Year -3: 25%; YEAR 2010 Year -2: 45%; YEAR 2011 Year -1: 30%
Revenues
Electricity | [5 empty] | 303.793 | 350.5304 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678 | 397.2678
Sulphur | [5 empty] | 0.52385 | 0.60444 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503 | 0.68503
Hydrogen | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating costs
Fuel (Coal) | [5 empty] | 101.148 | 116.7092 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704 | 132.2704
Maintenance | [5 empty] | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72 | 39.72
Labour | [5 empty] | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32
Chemicals and Consumables | [5 empty] | 2.8982 | 3.3441 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79 | 3.79
Waste Disposal | [5 empty] | 1.4349 | 1.6556 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764 | 1.8764
Insurance + Local Taxes | [5 empty] | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23 | 22.23
CO2 Emissions | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fixed Capital Expenditure |  |  | YEAR 2009 Year -3: 389.025; YEAR 2010 Year -2: 700.245; YEAR 2011 Year -1: 466.83
Total Cash Flow (yearly) |  |  | -389.025 | -700.245 | -466.83 | 128.5658 | 159.1559 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 189.746 | 0
Total Cash Flow (accumulated) |  |  | -389.025 | -1089.27 | -1556.1 | -1427.5342 | -1268.3784 | -1078.6324 | -888.8864 | -699.1404 | -509.3944 | -319.6484 | -129.9024 | 59.8436 | 249.5896 | 439.3356 | 629.0815 | 818.8275 | 1008.5735 | 1198.3195 | 1388.0655 | 1577.8115 | 1767.5575 | 1957.3035 | 2147.0495 | 2336.7955 | 2526.5415 | 2716.2875 | 2906.0334 | 3095.7794 | 3285.5254 | 3475.2714 | 3665.0174 | 3854.7634 | 4044.5094 | 4044.5094
Discounted Cash Flow (yearly) |  |  | -353.6591 | -578.7149 | -350.7363 | 87.8121 | 98.8233 | 107.1067 | 97.3697 | 88.5179 | 80.4708 | 73.1553 | 66.5048 | 60.4589 | 54.9627 | 49.966 | 45.4237 | 41.2943 | 37.5402 | 34.1275 | 31.025 | 28.2045 | 25.6405 | 23.3095 | 21.1905 | 19.2641 | 17.5128 | 15.9207 | 14.4734 | 13.1576 | 11.9615 | 10.8741 | 9.8855 | 8.9868 | 8.1698 | 0
Discounted Cash Flow (accumulated) |  |  | -353.6591 | -932.374 | -1283.1103 | -1195.2981 | -1096.4748 | -989.3682 | -891.9985 | -803.4806 | -723.0097 | -649.8545 | -583.3496 | -522.8907 | -467.9281 | -417.962 | -372.5383 | -331.2441 | -293.7038 | -259.5764 | -228.5514 | -200.3468 | -174.7064 | -151.3968 | -130.2063 | -110.9423 | -93.4295 | -77.5087 | -63.0354 | -49.8777 | -37.9163 | -27.0422 | -17.1567 | -8.1698 | -9.4147e-14 | -9.4147e-14
|  |  | YEAR 2030 Year 19: Hidden acc cf; YEAR 2032 Year 21: -110.9423; YEAR 2033 Year 22: -93.4295; YEAR 2034 Year 23: -77.5087; YEAR 2035 Year 24: -63.0354; YEAR 2036 Year 25: -49.8777; YEAR 2037 Year 26: -37.9163; YEAR 2038 Year 27: -27.0422; YEAR 2039 Year 28: -17.1567; YEAR 2040 Year 29: -8.1698; YEAR 2041 Year 30: -9.4147e-14; YEAR 2042 Year 31: -9.4147e-14 | -9.4147e-14

## IGCC wo CC
Production |  |  |  | Capital Expenditure |  | UK£ (million) |  | Operating Costs | UK£ (million/year) |  |  |  | Revenues
Coal feedrate | te/h | 230.7917 |  | Installed cost |  | 910 |  | Fuel Cost |  | 65 | UK£/te |  | Electricity Price |  | 0.059494 | UK£/kWh
Net power ouput | MW | 746.1 |  | Land purchase, surveys |  | 5% |  | Maintenance |  | 34.22 | UK£/year |  | Sulphur Price |  | 40 | UK£/te
Sulphur for export | te/h | 1.95 |  | Fees |  | 10% |  | CO2 Emissions |  | 0 | UK£/te |  | Hydrogen Price |  | 1307.1895 | UK£/te
|  |  |  | Contingencies |  | 25% |  | Labour Cost |  |  | UK£/year (million)
[8 empty] | Number of operations personnel |  |  | 115 |  | Discounted Rate: |  | 10%
|  |  |  | Total Investment Cost |  | 1274 |  | Average salary options personnel |  |  | 0.05 |  | Insurance |  | 2% | Installed Cost
[8 empty] | Admin |  |  | 30%
[8 empty] | Total Labour Cost |  |  | 7.475
YEAR
CASH FLOW ANALYSIS |  |  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
UK£ (million) |  |  | Year -3 | Year -2 | Year -1 | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31
Load factor - Hydrogen Production | [5 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Load factor - Power Island | [5 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Availability - Hydrogen Production | [5 empty] | 65% | 75% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
Availability - Power Island | [5 empty] | 65% | 75% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
Equivalent yearly hours - Hydrogen Production | [5 empty] | 5694 | 6570 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446
Equivalent yearly hours - Power Island | [5 empty] | 5694 | 6570 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446
Hydrogen Exported |  | tpa |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Expenditure factor |  |  | YEAR 2009 Year -3: 25%; YEAR 2010 Year -2: 45%; YEAR 2011 Year -1: 30%
Revenues
Electricity | [5 empty] | 252.7459 | 291.6298 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138 | 330.5138
Sulphur | [5 empty] | 0.44413 | 0.51246 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079 | 0.58079
Hydrogen | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating costs
Fuel (Coal) | [5 empty] | 85.4183 | 98.5596 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009 | 111.7009
Maintenance | [5 empty] | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22 | 34.22
Labour | [5 empty] | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475
Chemicals and Consumables | [5 empty] | 1.8965 | 2.1882 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48
Waste Disposal | [5 empty] | 1.2162 | 1.4034 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905 | 1.5905
Insurance + Local Taxes | [5 empty] | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2
CO2 Emissions | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fixed Capital Expenditure |  |  | YEAR 2009 Year -3: 318.5; YEAR 2010 Year -2: 573.3; YEAR 2011 Year -1: 382.2
Total Cash Flow (yearly) |  |  | -318.5 | -573.3 | -382.2 | 104.764 | 130.0961 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 155.4283 | 0
Total Cash Flow (accumulated) |  |  | -318.5 | -891.8 | -1274 | -1169.236 | -1039.1399 | -883.7116 | -728.2833 | -572.855 | -417.4268 | -261.9985 | -106.5702 | 48.8581 | 204.2864 | 359.7146 | 515.1429 | 670.5712 | 825.9995 | 981.4278 | 1136.8561 | 1292.2843 | 1447.7126 | 1603.1409 | 1758.5692 | 1913.9975 | 2069.4257 | 2224.854 | 2380.2823 | 2535.7106 | 2691.1389 | 2846.5672 | 3001.9954 | 3157.4237 | 3312.852 | 3312.852
Discounted Cash Flow (yearly) |  |  | -289.5455 | -473.8017 | -287.1525 | 71.5552 | 80.7795 | 87.7352 | 79.7593 | 72.5084 | 65.9168 | 59.9243 | 54.4767 | 49.5242 | 45.022 | 40.9291 | 37.2083 | 33.8257 | 30.7507 | 27.9551 | 25.4138 | 23.1034 | 21.0031 | 19.0937 | 17.3579 | 15.7799 | 14.3454 | 13.0413 | 11.8557 | 10.7779 | 9.7981 | 8.9074 | 8.0976 | 7.3615 | 6.6922 | 0
Discounted Cash Flow (accumulated) |  |  | -289.5455 | -763.3471 | -1050.4996 | -978.9444 | -898.165 | -810.4297 | -730.6705 | -658.162 | -592.2453 | -532.3209 | -477.8443 | -428.32 | -383.298 | -342.3689 | -305.1606 | -271.3348 | -240.5842 | -212.629 | -187.2153 | -164.1118 | -143.1087 | -124.015 | -106.6571 | -90.8771 | -76.5317 | -63.4904 | -51.6347 | -40.8568 | -31.0587 | -22.1513 | -14.0537 | -6.6922 | -4.496e-12 | -4.496e-12
|  |  | YEAR 2030 Year 19: Hidden acc cf; YEAR 2032 Year 21: -90.8771; YEAR 2033 Year 22: -76.5317; YEAR 2034 Year 23: -63.4904; YEAR 2035 Year 24: -51.6347; YEAR 2036 Year 25: -40.8568; YEAR 2037 Year 26: -31.0587; YEAR 2038 Year 27: -22.1513; YEAR 2039 Year 28: -14.0537; YEAR 2040 Year 29: -6.6922; YEAR 2041 Year 30: -4.496e-12; YEAR 2042 Year 31: -4.496e-12 | -4.496e-12

## CCGT w 90% CC
Production |  |  |  | Capital Expenditure |  | UK£ (million) |  | Operating Costs | UK£ (million/year) |  |  |  | Revenues
Nat Gas Feedrate | te/h | 127.9167 |  | Installed cost |  | 731.4 |  | Fuel Cost |  | 265 | UK£/te |  | Electricity Price |  | 0.069567 | UK£/kWh
Net power ouput | MW | 842.3 |  | Land purchase, surveys |  | 5% |  | Maintenance |  | 25.5 | UK£/year
|  |  |  | Fees |  | 10% |  | CO2 Emissions |  | 0 | UK£/te
|  |  |  | Contingencies |  | 25% |  | Labour Cost |  |  | UK£/year (million)
[8 empty] | Number of operations personnel |  |  | 60 |  | Discounted Rate: |  | 10%
|  |  |  | Total Investment Cost |  | 1023.96 |  | Average salary options personnel |  |  | 0.05 |  | Insurance |  | 2% | Installed Cost
[8 empty] | Admin |  |  | 30%
[8 empty] | Total Labour Cost |  |  | 3.9
YEAR
CASH FLOW ANALYSIS |  |  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
UK£ (million) |  |  | Year -3 | Year -2 | Year -1 | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21
Load factor | [5 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Availability | [5 empty] | 65% | 75% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
Equivalent yearly hours | [5 empty] | 5694 | 6570 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446
Expenditure factor |  |  | YEAR 2009 Year -3: 25%; YEAR 2010 Year -2: 45%; YEAR 2011 Year -1: 30%
Revenues
Electricity | [5 empty] | 333.6485 | 384.9791 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096 | 436.3096
Operating costs
Fuel (Natural Gas) | [5 empty] | 193.0147 | 222.7093 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039
Maintenance | [5 empty] | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
Labour | [5 empty] | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
Chemicals and Consumables | [5 empty] | 0.91765 | 1.0588 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Insurance + Local Taxes | [5 empty] | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628 | 14.628
CO2 Emissions | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fixed Capital Expenditure |  |  | YEAR 2009 Year -3: 255.99; YEAR 2010 Year -2: 460.782; YEAR 2011 Year -1: 307.188
Total Cash Flow (yearly) |  |  | -255.99 | -460.782 | -307.188 | 95.6882 | 117.183 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 138.6777 | 0
Total Cash Flow (accumulated) |  |  | -255.99 | -716.772 | -1023.96 | -928.2718 | -811.0889 | -672.4111 | -533.7334 | -395.0556 | -256.3779 | -117.7002 | 20.9776 | 159.6553 | 298.3331 | 437.0108 | 575.6886 | 714.3663 | 853.0441 | 991.7218 | 1130.3996 | 1269.0773 | 1407.7551 | 1546.4328 | 1685.1106 | 1685.1106
Discounted Cash Flow (yearly) |  |  | -232.7182 | -380.8116 | -230.7949 | 65.3563 | 72.7614 | 78.28 | 71.1636 | 64.6942 | 58.8129 | 53.4663 | 48.6057 | 44.187 | 40.17 | 36.5182 | 33.1984 | 30.1803 | 27.4367 | 24.9424 | 22.6749 | 20.6136 | 18.7396 | 17.036 | 15.4873 | 0
Discounted Cash Flow (accumulated) |  |  | -232.7182 | -613.5298 | -844.3246 | -778.9683 | -706.2069 | -627.927 | -556.7634 | -492.0692 | -433.2563 | -379.79 | -331.1843 | -286.9973 | -246.8273 | -210.3091 | -177.1107 | -146.9304 | -119.4938 | -94.5514 | -71.8764 | -51.2629 | -32.5233 | -15.4873 | 8.3311e-13 | 8.3311e-13
|  |  | YEAR 2030 Year 19: Hidden acc cf; YEAR 2032 Year 21: 8.3311e-13 | 8.3311e-13 | 8.3311e-13 | 8.3311e-13 | 8.3311e-13 | 8.3311e-13 | 8.3311e-13 | 8.3311e-13 | 8.3311e-13 | 8.3311e-13 | 8.3311e-13 | 8.3311e-13

## CCGT w 75% CC
Production |  |  |  | Capital Expenditure |  | UK£ (million) |  | Operating Costs | UK£ (million/year) |  |  |  | Revenues
Nat Gas Feedrate | te/h | 127.9167 |  | Installed cost |  | 696.9 |  | Fuel Cost |  | 265 | UK£/te |  | Electricity Price |  | 0.065892 | UK£/kWh
Net power ouput | MW | 872.3 |  | Land purchase, surveys |  | 5% |  | Maintenance |  | 24.6 | UK£/year
|  |  |  | Fees |  | 10% |  | CO2 Emissions |  | 0 | UK£/te
|  |  |  | Contingencies |  | 25% |  | Labour Cost |  |  | UK£/year (million)
[8 empty] | Number of operations personnel |  |  | 60 |  | Discounted Rate: |  | 10%
|  |  |  | Total Investment Cost |  | 975.66 |  | Average salary options personnel |  |  | 0.05 |  | Insurance |  | 2% | Installed Cost
[8 empty] | Admin |  |  | 30%
[8 empty] | Total Labour Cost |  |  | 3.9
YEAR
CASH FLOW ANALYSIS |  |  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
UK£ (million) |  |  | Year -3 | Year -2 | Year -1 | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21
Load factor | [5 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Availability | [5 empty] | 65% | 75% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
Equivalent yearly hours | [5 empty] | 5694 | 6570 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446
Expenditure factor |  |  | YEAR 2009 Year -3: 25%; YEAR 2010 Year -2: 45%; YEAR 2011 Year -1: 30%
Revenues
Electricity | [5 empty] | 327.2763 | 377.6265 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767 | 427.9767
Operating costs
Fuel (Natural Gas) | [5 empty] | 193.0147 | 222.7093 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039
Maintenance | [5 empty] | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6
Labour | [5 empty] | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
Chemicals and Consumables | [5 empty] | 0.74941 | 0.86471 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
Insurance + Local Taxes | [5 empty] | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938 | 13.938
CO2 Emissions | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fixed Capital Expenditure |  |  | YEAR 2009 Year -3: 243.915; YEAR 2010 Year -2: 439.047; YEAR 2011 Year -1: 292.698
Total Cash Flow (yearly) |  |  | -243.915 | -439.047 | -292.698 | 91.0741 | 111.6145 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 132.1548 | 0
Total Cash Flow (accumulated) |  |  | -243.915 | -682.962 | -975.66 | -884.5859 | -772.9714 | -640.8166 | -508.6618 | -376.5069 | -244.3521 | -112.1973 | 19.9575 | 152.1123 | 284.2671 | 416.4219 | 548.5767 | 680.7315 | 812.8863 | 945.0411 | 1077.1959 | 1209.3508 | 1341.5056 | 1473.6604 | 1605.8152 | 1605.8152
Discounted Cash Flow (yearly) |  |  | -221.7409 | -362.8488 | -219.9083 | 62.2049 | 69.3038 | 74.5979 | 67.8163 | 61.6512 | 56.0465 | 50.9514 | 46.3195 | 42.1086 | 38.2805 | 34.8005 | 31.6368 | 28.7607 | 26.1461 | 23.7692 | 21.6084 | 19.644 | 17.8582 | 16.2347 | 14.7588 | 0
Discounted Cash Flow (accumulated) |  |  | -221.7409 | -584.5897 | -804.498 | -742.2931 | -672.9893 | -598.3914 | -530.5751 | -468.9239 | -412.8773 | -361.9259 | -315.6065 | -273.4979 | -235.2174 | -200.4169 | -168.78 | -140.0193 | -113.8732 | -90.104 | -68.4956 | -48.8516 | -30.9935 | -14.7588 | 2.9097e-12 | 2.9097e-12
|  |  | YEAR 2030 Year 19: Hidden acc cf; YEAR 2032 Year 21: 2.9097e-12 | 2.9097e-12 | 2.9097e-12 | 2.9097e-12 | 2.9097e-12 | 2.9097e-12 | 2.9097e-12 | 2.9097e-12 | 2.9097e-12 | 2.9097e-12 | 2.9097e-12 | 2.9097e-12

## CCGT wo CC
Production |  |  |  | Capital Expenditure |  | UK£ (million) |  | Operating Costs | UK£ (million/year) |  |  |  | Revenues
Nat Gas Feedrate | te/h | 127.9167 |  | Installed cost |  | 388.9 |  | Fuel Cost |  | 265 | UK£/te |  | Electricity Price |  | 0.047883 | UK£/kWh
Net power ouput | MW | 990.8 |  | Land purchase, surveys |  | 5% |  | Maintenance |  | 16.6 | UK£/year
|  |  |  | Fees |  | 10% |  | CO2 Emissions |  | 0 | UK£/te
|  |  |  | Contingencies |  | 25% |  | Labour Cost |  |  | UK£/year (million)
[8 empty] | Number of operations personnel |  |  | 40 |  | Discounted Rate: |  | 10%
|  |  |  | Total Investment Cost |  | 544.46 |  | Average salary options personnel |  |  | 0.05 |  | Insurance |  | 2% | Installed Cost
[8 empty] | Admin |  |  | 30%
[8 empty] | Total Labour Cost |  |  | 2.6
YEAR
CASH FLOW ANALYSIS |  |  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
UK£ (million) |  |  | Year -3 | Year -2 | Year -1 | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21
Load factor | [5 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Availability | [5 empty] | 65% | 75% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
Equivalent yearly hours | [5 empty] | 5694 | 6570 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446
Expenditure factor |  |  | YEAR 2009 Year -3: 25%; YEAR 2010 Year -2: 45%; YEAR 2011 Year -1: 30%
Revenues
Electricity | [5 empty] | 270.1369 | 311.6964 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559 | 353.2559
Operating costs
Fuel (Natural Gas) | [5 empty] | 193.0147 | 222.7093 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039 | 252.4039
Maintenance | [5 empty] | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6
Labour | [5 empty] | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
Chemicals and Consumables | [5 empty] | 0.00076471 | 0.00088235 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001
Insurance + Local Taxes | [5 empty] | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778 | 7.778
CO2 Emissions | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fixed Capital Expenditure |  |  | YEAR 2009 Year -3: 136.115; YEAR 2010 Year -2: 245.007; YEAR 2011 Year -1: 163.338
Total Cash Flow (yearly) |  |  | -136.115 | -245.007 | -163.338 | 50.1434 | 62.0082 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 73.873 | 0
Total Cash Flow (accumulated) |  |  | -136.115 | -381.122 | -544.46 | -494.3166 | -432.3084 | -358.4353 | -284.5623 | -210.6892 | -136.8162 | -62.9431 | 10.9299 | 84.803 | 158.676 | 232.5491 | 306.4221 | 380.2952 | 454.1682 | 528.0412 | 601.9143 | 675.7873 | 749.6604 | 823.5334 | 897.4065 | 897.4065
Discounted Cash Flow (yearly) |  |  | -123.7409 | -202.4851 | -122.7183 | 34.2486 | 38.5022 | 41.6994 | 37.9086 | 34.4623 | 31.3294 | 28.4813 | 25.8921 | 23.5382 | 21.3984 | 19.4531 | 17.6846 | 16.0769 | 14.6154 | 13.2867 | 12.0788 | 10.9808 | 9.9825 | 9.075 | 8.25 | 0
Discounted Cash Flow (accumulated) |  |  | -123.7409 | -326.226 | -448.9443 | -414.6957 | -376.1935 | -334.494 | -296.5855 | -262.1232 | -230.7938 | -202.3125 | -176.4205 | -152.8822 | -131.4838 | -112.0308 | -94.3461 | -78.2692 | -63.6538 | -50.3671 | -38.2883 | -27.3075 | -17.325 | -8.25 | 1.0658e-13 | 1.0658e-13
|  |  | YEAR 2030 Year 19: Hidden acc cf; YEAR 2032 Year 21: 1.0658e-13 | 1.0658e-13 | 1.0658e-13 | 1.0658e-13 | 1.0658e-13 | 1.0658e-13 | 1.0658e-13 | 1.0658e-13 | 1.0658e-13 | 1.0658e-13 | 1.0658e-13 | 1.0658e-13

## USCPC w CC
Production |  |  |  | Capital Expenditure |  | UK£ (million) |  | Operating Costs | UK£ (million/year) |  |  |  | Revenues
Coal Feedrate | te/h | 256.7917 |  | Installed cost |  | 1148.2 |  | Fuel Cost |  | 65 | UK£/te |  | Electricity Price |  | 0.087313 | UK£/kWh
Net Power Ouput | MW | 626.7 |  | Land purchase, surveys |  | 5% |  | Maintenance |  | 40.1 | UK£/year
|  |  |  | Fees |  | 10% |  | CO2 Emissions |  | 0 | UK£/te
|  |  |  | Contingencies |  | 25% |  | Labour Cost |  |  | UK£/year (million)
[8 empty] | Number of operations personnel |  |  | 115 |  | Discounted Rate: |  | 10%
|  |  |  | Total Investment Cost |  | 1607.48 |  | Average salary options personnel |  |  | 0.05 |  | Insurance |  | 2% | Installed Cost
[8 empty] | Admin |  |  | 30%
[8 empty] | Total Labour Cost |  |  | 7.475
YEAR
CASH FLOW ANALYSIS |  |  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
UK£ (million) |  |  | Year -3 | Year -2 | Year -1 | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31
Load factor | [5 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Availability | [5 empty] | 65% | 75% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
Equivalent yearly hours | [5 empty] | 5694 | 6570 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446
Expenditure factor |  |  | YEAR 2009 Year -3: 25%; YEAR 2010 Year -2: 45%; YEAR 2011 Year -1: 30%
Revenues
Electricity | [5 empty] | 311.571 | 359.505 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439 | 407.439
Operating costs
Fuel (Coal) | [5 empty] | 95.0412 | 109.6629 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846
Maintenance | [5 empty] | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1
Labour | [5 empty] | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475 | 7.475
Chemicals and Consumables | [5 empty] | 11.6235 | 13.4118 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2
Waste Disposal | [5 empty] | 1.1274 | 1.3009 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743
Insurance + Local Taxes | [5 empty] | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964 | 22.964
CO2 Emissions | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fixed Capital Expenditure |  |  | YEAR 2009 Year -3: 401.87; YEAR 2010 Year -2: 723.366; YEAR 2011 Year -1: 482.244
Total Cash Flow (yearly) |  |  | -401.87 | -723.366 | -482.244 | 133.2399 | 164.5905 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 195.9411 | 0
Total Cash Flow (accumulated) |  |  | -401.87 | -1125.236 | -1607.48 | -1474.2401 | -1309.6496 | -1113.7085 | -917.7674 | -721.8263 | -525.8852 | -329.9441 | -134.003 | 61.9381 | 257.8792 | 453.8203 | 649.7614 | 845.7025 | 1041.6436 | 1237.5847 | 1433.5258 | 1629.4669 | 1825.408 | 2021.3491 | 2217.2902 | 2413.2313 | 2609.1724 | 2805.1135 | 3001.0546 | 3196.9957 | 3392.9368 | 3588.8779 | 3784.819 | 3980.7601 | 4176.7012 | 4176.7012
Discounted Cash Flow (yearly) |  |  | -365.3364 | -597.8231 | -362.3171 | 91.0046 | 102.1978 | 110.6036 | 100.5488 | 91.408 | 83.0982 | 75.5438 | 68.6762 | 62.4329 | 56.7572 | 51.5974 | 46.9067 | 42.6425 | 38.7659 | 35.2417 | 32.0379 | 29.1254 | 26.4776 | 24.0706 | 21.8823 | 19.893 | 18.0846 | 16.4405 | 14.9459 | 13.5872 | 12.352 | 11.2291 | 10.2083 | 9.2802 | 8.4366 | 0
Discounted Cash Flow (accumulated) |  |  | -365.3364 | -963.1595 | -1325.4766 | -1234.4719 | -1132.2742 | -1021.6705 | -921.1218 | -829.7138 | -746.6156 | -671.0719 | -602.3957 | -539.9628 | -483.2057 | -431.6083 | -384.7015 | -342.059 | -303.2931 | -268.0514 | -236.0135 | -206.8881 | -180.4104 | -156.3399 | -134.4575 | -114.5645 | -96.4799 | -80.0394 | -65.0934 | -51.5062 | -39.1542 | -27.9251 | -17.7168 | -8.4366 | -2.8226e-12 | -2.8226e-12
|  |  | YEAR 2030 Year 19: Hidden acc cf; YEAR 2032 Year 21: -114.5645; YEAR 2033 Year 22: -96.4799; YEAR 2034 Year 23: -80.0394; YEAR 2035 Year 24: -65.0934; YEAR 2036 Year 25: -51.5062; YEAR 2037 Year 26: -39.1542; YEAR 2038 Year 27: -27.9251; YEAR 2039 Year 28: -17.7168; YEAR 2040 Year 29: -8.4366; YEAR 2041 Year 30: -2.8226e-12; YEAR 2042 Year 31: -2.8226e-12 | -2.8226e-12

## USCPC wo CC
Production |  |  |  | Capital Expenditure |  | UK£ (million) |  | Operating Costs | UK£ (million/year) |  |  |  | Revenues
Coal feedrate | te/h | 256.7917 |  | Installed cost |  | 814.1 |  | Fuel Cost |  | 65 | UK£/te |  | Electricity Price |  | 0.056238 | UK£/kWh
Net power ouput | MW | 779.2 |  | Land purchase, surveys |  | 5% |  | Maintenance |  | 32.6 | UK£/year
|  |  |  | Fees |  | 10% |  | CO2 Emissions |  | 0 | UK£/te
|  |  |  | Contingencies |  | 25% |  | Labour Cost |  |  | UK£/year (million)
[8 empty] | Number of operations personnel |  |  | 105 |  | Discounted Rate: |  | 10%
|  |  |  | Total Investment Cost |  | 1139.74 |  | Average salary options personnel |  |  | 0.05 |  | Insurance |  | 2% | Installed Cost
[8 empty] | Admin |  |  | 30%
[8 empty] | Total Labour Cost |  |  | 6.825
YEAR
CASH FLOW ANALYSIS |  |  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
UK£ (million) |  |  | Year -3 | Year -2 | Year -1 | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31
Load factor | [5 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Availability | [5 empty] | 65% | 75% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
Equivalent yearly hours | [5 empty] | 5694 | 6570 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446
Expenditure factor |  |  | YEAR 2009 Year -3: 25%; YEAR 2010 Year -2: 45%; YEAR 2011 Year -1: 30%
Revenues
Electricity | [5 empty] | 249.5135 | 287.9002 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869 | 326.2869
Operating costs
Fuel (Coal) | [5 empty] | 95.0412 | 109.6629 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846 | 124.2846
Maintenance | [5 empty] | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6 | 32.6
Labour | [5 empty] | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825 | 6.825
Chemicals and Consumables | [5 empty] | 4.3588 | 5.0294 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7
Waste Disposal | [5 empty] | 1.1274 | 1.3009 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743
Insurance + Local Taxes | [5 empty] | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282 | 16.282
CO2 Emissions | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fixed Capital Expenditure |  |  | YEAR 2009 Year -3: 284.935; YEAR 2010 Year -2: 512.883; YEAR 2011 Year -1: 341.922
Total Cash Flow (yearly) |  |  | -284.935 | -512.883 | -341.922 | 93.2791 | 116.2001 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 139.121 | 0
Total Cash Flow (accumulated) |  |  | -284.935 | -797.818 | -1139.74 | -1046.4609 | -930.2608 | -791.1398 | -652.0187 | -512.8977 | -373.7767 | -234.6556 | -95.5346 | 43.5864 | 182.7074 | 321.8285 | 460.9495 | 600.0705 | 739.1915 | 878.3126 | 1017.4336 | 1156.5546 | 1295.6757 | 1434.7967 | 1573.9177 | 1713.0387 | 1852.1598 | 1991.2808 | 2130.4018 | 2269.5228 | 2408.6439 | 2547.7649 | 2686.8859 | 2826.007 | 2965.128 | 2965.128
Discounted Cash Flow (yearly) |  |  | -259.0318 | -423.8702 | -256.8911 | 63.7109 | 72.1511 | 78.5302 | 71.3911 | 64.901 | 59.0009 | 53.6372 | 48.7611 | 44.3282 | 40.2984 | 36.6349 | 33.3045 | 30.2768 | 27.5244 | 25.0221 | 22.7474 | 20.6795 | 18.7995 | 17.0905 | 15.5368 | 14.1243 | 12.8403 | 11.673 | 10.6118 | 9.6471 | 8.7701 | 7.9728 | 7.248 | 6.5891 | 5.9901 | 0
Discounted Cash Flow (accumulated) |  |  | -259.0318 | -682.9021 | -939.7931 | -876.0822 | -803.9311 | -725.4009 | -654.0098 | -589.1088 | -530.108 | -476.4708 | -427.7097 | -383.3815 | -343.083 | -306.4481 | -273.1437 | -242.8669 | -215.3425 | -190.3204 | -167.573 | -146.8935 | -128.094 | -111.0036 | -95.4668 | -81.3424 | -68.5021 | -56.8291 | -46.2173 | -36.5702 | -27.8001 | -19.8272 | -12.5792 | -5.9901 | -5.3735e-13 | -5.3735e-13
|  |  | YEAR 2030 Year 19: Hidden acc cf; YEAR 2032 Year 21: -81.3424; YEAR 2033 Year 22: -68.5021; YEAR 2034 Year 23: -56.8291; YEAR 2035 Year 24: -46.2173; YEAR 2036 Year 25: -36.5702; YEAR 2037 Year 26: -27.8001; YEAR 2038 Year 27: -19.8272; YEAR 2039 Year 28: -12.5792; YEAR 2040 Year 29: -5.9901; YEAR 2041 Year 30: -5.3735e-13; YEAR 2042 Year 31: -5.3735e-13 | -5.3735e-13

## OXYFUEL with CC
Production |  |  |  | Capital Expenditure |  | UK£ (million) |  | Operating Costs | UK£ (million/year) |  |  |  | Revenues
Coal feedrate | te/h | 257 |  | Installed cost |  | 1354.7 |  | Fuel Cost |  | 65 | UK£/te |  | Electricity Price |  | 0.096898 | UK£/kWh
Net power ouput | MW | 605.6 |  | Land purchase, surveys |  | 5% |  | Maintenance |  | 44.5 | UK£/year
|  |  |  | Fees |  | 10% |  | CO2 Emissions |  | 0 | UK£/te
|  |  |  | Contingencies |  | 25% |  | Labour Cost |  |  | UK£/year (million)
[8 empty] | Number of operations personnel |  |  | 128 |  | Discounted Rate: |  | 10%
|  |  |  | Total Investment Cost |  | 1896.58 |  | Average salary options personnel |  |  | 0.05 |  | Insurance |  | 2% | Installed Cost
[8 empty] | Admin |  |  | 30%
[8 empty] | Total Labour Cost |  |  | 8.32
YEAR
CASH FLOW ANALYSIS |  |  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
UK£ (million) |  |  | Year -3 | Year -2 | Year -1 | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31
Load factor | [5 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Availability | [5 empty] | 65% | 75% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85%
Equivalent yearly hours | [5 empty] | 5694 | 6570 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446 | 7446
Expenditure factor |  |  | YEAR 2009 Year -3: 25%; YEAR 2010 Year -2: 45%; YEAR 2011 Year -1: 30%
Revenues
Electricity | [5 empty] | 334.1315 | 385.5363 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412 | 436.9412
Operating costs
Fuel (Coal) | [5 empty] | 95.1183 | 109.7519 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854 | 124.3854
Maintenance | [5 empty] | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5
Labour | [5 empty] | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32
Chemicals and Consumables | [5 empty] | 0.076471 | 0.088235 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Waste Disposal | [5 empty] | 1.1274 | 1.3009 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743 | 1.4743
Insurance + Local Taxes | [5 empty] | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094 | 27.094
CO2 Emissions | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fixed Capital Expenditure |  |  | YEAR 2009 Year -3: 474.145; YEAR 2010 Year -2: 853.461; YEAR 2011 Year -1: 568.974
Total Cash Flow (yearly) |  |  | -474.145 | -853.461 | -568.974 | 157.8953 | 194.4814 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 231.0674 | 0
Total Cash Flow (accumulated) |  |  | -474.145 | -1327.606 | -1896.58 | -1738.6847 | -1544.2033 | -1313.1358 | -1082.0684 | -851.0009 | -619.9335 | -388.866 | -157.7986 | 73.2689 | 304.3363 | 535.4038 | 766.4712 | 997.5386 | 1228.6061 | 1459.6735 | 1690.741 | 1921.8084 | 2152.8759 | 2383.9433 | 2615.0108 | 2846.0782 | 3077.1457 | 3308.2131 | 3539.2806 | 3770.348 | 4001.4154 | 4232.4829 | 4463.5503 | 4694.6178 | 4925.6852 | 4925.6852
Discounted Cash Flow (yearly) |  |  | -431.0409 | -705.3397 | -427.4786 | 107.8446 | 120.7576 | 130.4315 | 118.5741 | 107.7947 | 97.9952 | 89.0865 | 80.9877 | 73.6252 | 66.932 | 60.8473 | 55.3157 | 50.287 | 45.7155 | 41.5595 | 37.7814 | 34.3467 | 31.2243 | 28.3857 | 25.8052 | 23.4593 | 21.3266 | 19.3878 | 17.6253 | 16.023 | 14.5664 | 13.2421 | 12.0383 | 10.9439 | 9.949 | 0
Discounted Cash Flow (accumulated) |  |  | -431.0409 | -1136.3806 | -1563.8592 | -1456.0145 | -1335.2569 | -1204.8253 | -1086.2512 | -978.4565 | -880.4614 | -791.3749 | -710.3871 | -636.7619 | -569.8299 | -508.9826 | -453.6669 | -403.3799 | -357.6645 | -316.1049 | -278.3236 | -243.9769 | -212.7526 | -184.3669 | -158.5617 | -135.1024 | -113.7758 | -94.388 | -76.7627 | -60.7397 | -46.1734 | -32.9312 | -20.8929 | -9.949 | 5.187e-13 | 5.187e-13
|  |  | YEAR 2030 Year 19: Hidden acc cf; YEAR 2032 Year 21: -135.1024; YEAR 2033 Year 22: -113.7758; YEAR 2034 Year 23: -94.388; YEAR 2035 Year 24: -76.7627; YEAR 2036 Year 25: -60.7397; YEAR 2037 Year 26: -46.1734; YEAR 2038 Year 27: -32.9312; YEAR 2039 Year 28: -20.8929; YEAR 2040 Year 29: -9.949; YEAR 2041 Year 30: 5.187e-13; YEAR 2042 Year 31: 5.187e-13 | 5.187e-13

## Summary Results
|  | IGCC w CC | IGCC w/o CC | USCPC w CC | USCPC wo CC | CCGT w 90% CC | CCGT w 75% CC | CCGT w/o CC | Oxyfuel
|  | Case 1A | Case 1B | Case 2A | Case 2B | Case 3A | Case 3A(ii) | Case 3B | Case 4
Power Production | MWgross | 923.8 | 878.1 | 745.7 | 836.2 | 955.3 | 970.7 | 1037.6 | 855.4
| MWnet | 700.1 | 746.1 | 626.7 | 779.2 | 842.3 | 872.3 | 990.8 | 605.6
Electricity Production Cost | £ / MWh | 76.2079 | 59.4935 | 87.3132 | 56.2377 | 69.5673 | 65.8918 | 47.8829 | 96.8978
CO2 Produced | te/h | 647.2083 | 548 | 608.1667 | 608 | 346.8333 | 347.1 | 347 | 607.9
CO2 Captured | te/h | 582.3333 | 0 | 547.1667 | 0 | 312.8333 | 261.1 | 0 | 549.3167
Carbon Capture Efficiency | % | 90 | 0 | 90 | 0 | 90 | 75 | 0 | 90
CO2 Emitted | te/h | 64.875 | 548 | 61 | 608 | 34 | 86 | 347 | 58.5833
CO2 Emissions Cost | £ / te CO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific CO2 Emissions (Gross) | g / KWhgross | 70.2262 | 624.0747 | 81.8023 | 727.0988 | 35.5909 | 88.5959 | 334.4256 | 68.4865
Specific CO2 Emissions (Net) | g / Kwhnet | 92.6653 | 734.486 | 97.3352 | 780.2875 | 40.3657 | 98.5899 | 350.222 | 96.736
CO2 Captured (Removed) Cost | £ / te | 20.0946 | n/a | 35.5924 | n/a | 58.3849 | 60.1652 | n/a | 44.8262
CO2 Avoided Cost | £ / te | 26.0422 | n/a | 45.5017 | n/a | 69.982 | 71.5683 | n/a | 59.4836
Cost of CO2 Captured (Removed) and Avoided
CO2 Captured (Removed) costs are calculated using the following equation:
| CO2 Captured (Removed) [£ / te] = |  |  | (Electricty Costw CO2 removal - Electricity Cost w/o CO2 removal) [ £ / kWh ]
CO2 removed [ te / kWh ]
CO2 Avoided costs are calculated using the following equation:
| CO2 Avoided [£ / te] = |  |  | (Electricty Costw CO2 removal - Electricity Cost w/o CO2 removal) [ £ / kWh ]
(Specific Emissionswo CO2 removal - Specifc Emissionsw CO2 removal) [ te / kWh ]